## Slide 1: IntelliFRA: An AI-Based Platform for Automated Transformer Fault Analysis
Department of Information Technology
B.Tech. Final Year Project Presentation | Academic Year 2024–25
Stage: Final Review / Project Defense
Presented by
Harini Panigrahi
Neha Verma
Prapti Bhayde
Yooraj Gole
Under the guidance of
Prof. Bhanu Tekwani
Vidyalankar Institute of Technology, Wadala, Mumbai

## Slide 2: Outline
01
Introduction
02
Problem Statement & Motivation
03
Objectives
04
Literature Survey
05
Research Gaps
06
Proposed System Architecture
07
Methodology
08
Dataset & Tools
09
Results & Discussion
10
Conclusion & Future Scope
11
Publications
12
References

## Slide 3: Introduction
01
Section
Duplicate this slide to introduce each major part of the talk.

## Slide 4: Introduction
Critical Grid Infrastructure: High-voltage power transformers are irreplaceable grid nodes; unexpected internal mechanical failures cause prolonged outages and multimillion-dollar losses.
Sweep Frequency Response Analysis (SFRA): Standardized under IEC 60076-18 as the premier non-intrusive electrical test for detecting internal core/winding mechanical deformation.
Operational Bottleneck: Field engineers currently rely on manual visual trace overlays and scalar indices (CC, ASLE) that cannot reliably distinguish operational noise from real structural damage.
IntelliFRA Solution: An open-source AI platform integrating 1D-CNN severity classification, Autoencoder anomaly gating, and interactive web visualization for real-time substation triage.
Fig. 1: IntelliFRA Interactive Web Diagnostic View (500-pt Recharts trace & CEA recommendations)

## Slide 5: Problem Statement & Motivation
Problem Statement
To design, develop, and benchmark an automated, end-to-end AI diagnostic platform capable of ingesting raw SFRA magnitude files (CSV/TXT), standardizing variable frequency samples, classifying winding mechanical faults into four severity grades with high accuracy, and detecting out-of-distribution anomalous signatures without requiring historical baseline curves—all executing with sub-millisecond CPU latency across an authenticated web application.
Motivation
Grid Reliability & Financial Impact: Manufacturing lead times for transmission transformers exceed 12 months. Early mechanical detection prevents catastrophic dielectric breakdown and millions in equipment replacement costs.
Inadequacy of Traditional Metrics: Scalar indices (CC, ASLE) require manual cutoff threshold tuning per transformer family, often failing to separate operational noise from true physical faults.
Closed-Set ML Fragility: Standard supervised neural networks blindly force every input into predefined training labels; unsupervised anomaly gating is critical to detect unknown winding topologies.
Operational Need: Substation crews need an instant screening tool to immediately greenlight healthy units and escalate genuine fault signatures without waiting weeks for expert report overlays.

## Slide 6: Objectives
1
To simulate and generate a physics-informed synthetic dataset of 50,000 SFRA curves across six degradation archetypes (NF, DLF, LCF, RDF, IDF, SCF) on a logarithmic frequency grid (1 kHz–2 MHz).
2
To design and train a dual-AI diagnostic pipeline: a 140,644-parameter 1D-CNN for severity classification and a 312,532-parameter dense Autoencoder for unsupervised out-of-distribution anomaly gating.
3
To implement multi-tiered fail-safe guardrails: incorporating discrete first-difference morphological filters (smoothness, monotonicity, peak counts) and deterministic FFT spectral fallbacks.
4
To deploy an auditable, authenticated web platform (FastAPI + React 19 + SQLite) providing sub-millisecond CPU execution, interactive Recharts visualization, and tenant data isolation.

## Slide 7: Literature Survey
Sr. | Author(s) & Year | Method / Technique | Dataset | Result | Limitation
1 | Ryder (2003) [1] | SFRA principles & scalar indicators (CC, ASLE) | Field utility transformer sweeps | Establishes baseline transfer-function mapping | Sensitive to test-lead noise; requires subjective human thresholds
2 | Shintemirov et al. (2010) [3] | Sub-band correlation & evidential reasoning | Lab winding models & simulation | Improved condition grading across discrete sub-bands | Fails on compound multi-mode deformations; rigid sub-band boundaries
3 | Secue & Mombello (2008) [11] | Resonance pole tracking & band deviation | Physical test transformers | Classified axial vs. radial winding deformations | Requires historical baseline from the identical physical unit
4 | Ince, Kiranyaz et al. (2016) [15] | 1D-CNN on raw waveforms without manual features | Motor current benchmark waveforms | Adaptive localized spectral feature learning from raw data | Evaluated solely on motor drives; not applied to transformer SFRA
5 | Phillip, Singh & Ramlal (2025) [6, 10] | Deep learning for narrow-band transformer FRA | Simulated & narrow-band field data | High classification accuracy on isolated frequency bands | Closed-set only; lacks anomaly gating, web interface & fail-safes

## Slide 8: Research Gaps Identified
1
Closed-Set Classifier Fragility
Supervised models force all inputs into predefined training categories, blindly misclassifying unfamiliar winding topologies, sensor noise, or unmodeled failure modes as normal or wrong fault grades.
2
Hand-Crafted Feature Dependency
Conventional techniques rely on rigid sub-band segmentation or scalar metrics (ASLE, CC) that require manual threshold tuning and fail to generalize across different MVA ratings and voltage classes.
3
Lack of Production-Ready Systems
Prior studies stop at offline Jupyter notebooks without building an auditable, end-to-end deployable platform with fail-safe fallbacks, sub-millisecond CPU latency, and interactive visualization for field crews.

## Slide 9: Proposed System Architecture
Input Ingestion
• CSV / TXT format auto-detect
• Minimum 50 valid float points
• Memory-bounded parsing
Preprocessing
• Edge-value pad to 500 points
• Per-sample Z-Score scaling
• Eliminates MVA gain offsets
Dual-AI Engine
• 1D-CNN (140k params; 4 classes)
• Autoencoder (312k params; anomaly)
• Zero missed critical faults
Multi-Tier Guardrails
• Morphological shape filters
• Monotonicity & peak checks
• Deterministic FFT fallback
Storage & UI Dashboard
• FastAPI async REST endpoints
• SQLite tenant-isolated DB
• React 19 & Recharts UI
Fig. 2: IntelliFRA End-to-End Five-Stage Ingestion, Inference, and Triage Architecture

## Slide 10: Methodology
1
Physics-Based Data Synthesis
Stochastic lumped-mode generator spanning 1 kHz–2 MHz. Superimposes 8–12 Lorentzian modes across 6 physical fault archetypes (50,000 curves total).
2
Standardization & Preprocessing
Robust CSV/TXT parsing, boundary edge-value replication to 500 samples, and independent per-sample z-score normalization (μ=0, σ=1, ε=1e-6).
3
Dual Neural Architecture
1D-CNN (140,644 parameters) with 3 Conv blocks and Dropout (p=0.2) + Dense Autoencoder (312,532 parameters) trained strictly on healthy baselines.
4
Training & Validation Rigor
PyTorch, Adam (lr=1e-3, 20 epochs), 80:20 split (40k/10k). Supplementary 5-fold cross-validation on 12k uncapped sweeps and shifted OOD test set.
5
Guardrails & Production UI
Morphological filters (smoothness, monotonicity, peak counts) + FFT fallback, integrated into FastAPI REST API and React 19 interactive Recharts UI.

## Slide 11: Dataset & Tools Used
Dataset
Name | IntelliFRA Physics-Synthesized SFRA Corpus
Source | Physics-informed stochastic lumped-mode generator (1 kHz–2 MHz)
No. of samples | 50,000 curves (12,500 per operational severity class)
No. of classes | 4 Classes: Normal, Minor Deviation, Moderate Fault, High Fault Risk
Train / Test split | 80:20 Split (40,000 Train / 10,000 Validation) + 5-Fold CV (12,000 sweeps)
Tools & Technologies
Languages & AI Frameworks: Python 3.10, PyTorch, Scikit-learn, NumPy, SciPy
Backend & Storage: FastAPI (asynchronous REST), SQLAlchemy, SQLite, Pydantic, Uvicorn, Bcrypt, JWT Authentication
Frontend & Visualization: React 19, Vite, Tailwind CSS, Recharts, Framer Motion, Lucide Icons
Optimization & Metrics: Adam optimizer (lr=1e-3), Cross-Entropy & MSE loss, single-core CPU latency profiling

## Slide 12: Results
94.41%
1D-CNN Validation Accuracy
(Macro F1 = 0.9443; Support = 10,000)
98.47%
Autoencoder Anomaly Accuracy
(100% Fault Recall across 7,497 faults)
0.274 ms
Full-Pipeline CPU Latency
(Sub-millisecond real-time triage)

## Slide 13: Comparison with Existing Methods
Method | Accuracy (%) | Precision (%) | Recall (%) | F1-score (%)
Proposed 1D-CNN (IntelliFRA) | 81.03% (94.41%*) | 82.80% (94.43%*) | 81.90% (94.41%*) | 82.34% (94.43%*)
Random Forest (100 trees, depth 15) | 72.57% ± 1.05% | 73.50% | 72.60% | 73.00%
SVM (RBF Kernel, C=1.0) | 66.13% ± 0.65% | 67.80% | 66.20% | 67.20%
Multilayer Perceptron (MLP 128-64) | 64.95% ± 0.94% | 65.90% | 64.90% | 65.30%
* Benchmark on 12,000 uncapped sweeps under 5-fold stratified cross-validation; 94.41% accuracy on the 10,000-sweep held-out split. On a separate shifted test set (±15% pole shift, heavy noise), 1D-CNN leads with 56.88% (vs. RF 51.21%, SVM 50.83%, MLP 49.33%).

## Slide 14: Conclusion & Future Scope
Conclusion
• Automated Triage: Successfully engineered an intelligent web platform that removes human subjectivity and manual overlay bottlenecks in transformer SFRA testing.
• High Classification & Zero-Miss Recall: 1D-CNN achieves 94.41% validation accuracy, while the Autoencoder flags anomalies with 98.47% accuracy and 100% recall on faulty sweeps.
• Sub-Millisecond Inference: Full-pipeline CPU execution in 0.274 ms with multi-tiered morphological filters and deterministic FFT spectral energy fail-safes.
• Complete B.Tech. Objective Fulfillment: All project objectives completed, delivering a deployable, open-source React/FastAPI tool for power utilities.
Future Scope
• Utility Field Fine-Tuning: Transfer learning and domain adaptation on measured substation SFRA recordings (IEEE DataPort and Indian utility fleets).
• Automated Inspection Reports: Adding one-click PDF engineering diagnostic report generation and automated three-phase baseline curve overlays.
• Adaptive Envelopes & Lab Testbed: Upgrading heuristic shape overrides with adaptive envelope trackers and physical laboratory winding testbed validation.

## Slide 15: Publications & Competitions
Paper(s)
Harini Panigrahi, Neha Verma, Prapti Bhayde, Yooraj Gole, and Bhanu Tekwani*, “IntelliFRA: An AI-Based Platform for Automated Transformer Fault Analysis,” International Conference on Trends in Electrical, Electronics and Computer Systems (ITEECS 2025). (Status: Submitted / Under Review | Length: ~8.5 pages)
Competitions
• Final Year Capstone Project, Department of Information Technology, Vidyalankar Institute of Technology, Mumbai (Academic Year 2024–25). • Selected for Institutional B.Tech. Final Review Showcase and Research Presentation.

## Slide 16: References
[1] S. A. Ryder, “Diagnosing Transformer Faults Using Frequency Response Analysis,” IEEE Electrical Insulation Magazine, vol. 19, no. 2, pp. 16–22, 2003.
[2] IEC 60076-18, “Power Transformers - Part 18: Measurement of Frequency Response,” International Electrotechnical Commission (IEC), Geneva, Switzerland, 2012.
[3] T. Ince, S. Kiranyaz et al., “Real-Time Motor Fault Detection by 1-D Convolutional Neural Networks,” IEEE Trans. Ind. Electron., vol. 63, no. 11, pp. 7067–7075, 2016.
[4] M. Sakurada and T. Yairi, “Anomaly Detection Using Autoencoders with Nonlinear Dimensionality Reduction,” in Proc. MLSDA, Gold Coast, Australia, pp. 4–11, 2014.
[5] M. Phillip, A. Singh, and C. J. Ramlal, “Towards Automated Frequency Response Analysis of Power Transformers with Deep Learning,” Applied Artificial Intelligence, vol. 39, no. 1, 2025.

## Slide 17
Thank You
Questions & Suggestions
Department of Information Technology | Vidyalankar Institute of Technology, Mumbai
Project Team: Harini Panigrahi, Neha Verma, Prapti Bhayde, Yooraj Gole | Guide: Prof. Bhanu Tekwani (bhanu.tekwani@vit.edu.in)